## Checklist
Data Center Decommission Plan Checklist
The following is based on +30 years working with data centers. In the Response column, choose from a drop down list. "Not Addressed" and "TBD" responses will auto-color red and yellow and be tallied below. For questions, please call Tad Davies, 314-265-2735.
Aspect | Element | Possible Issue | Response
Real Estate
RE.1 | Lease | Have you reviewed the lease agreement? | Not Addressed
RE.2 |  | Are there requirements to return the space to its original condition?
Decommission Plan (DP)
DP.1 |  | Have you confirmed that the space can be left "as is"?
DP.2 |  | Has your DP been submitted to the Property Manager?
DP.3 |  | Has your DP been approved in writing by your Property Manager?
DP.4 |  | Has your DP been reviewed by the AHJ (Authority Having Jurisdiction)? [typically Fire Marshall]
DP.5 |  | Have you informed your insurance carrier that there will no longer be a data center located in your space?
DP.6 |  | Have you determined to manage the plan internally or use 3rd-party expert?
DP.7 |  | Do you have a project schedule that reflects planning, permitting, stakeholder review, contractor acquistion/work, and IT work?
DP.8 |  | Have you determined what work will need to occur off-hours?
Scope of Work
SOW.1 | Contractor SOW | After contractor clean-up, do you have a data center cleaning company perform a deep clean?
SOW.2 |  | Do you have written SOWs from contractors?
SOW.3 |  | Does the SOW address the proper disposal of equipment?
SOW.4 |  | Will the contractor provide a Certificate of Insurance naming your company as additional insured?
SOW.5 |  | Does the contractor(s) have expertise in data center work?
SOW.6 |  | Will permits be required?
SOW.7 |  | Is over-time included for off-hours work?
SOW.8 |  | Is path of equipment removal described?
SOW.9 |  | If an elevator is needed, does it have sufficient size and weight capacity?
SOW.10 |  | Will the loss of an elevator dictate the work be completed off-hours?
SOW.11 |  | Is projection of existing finishes (floors, walls, elevators) included?
SOW.12 |  | Provisions to address the roof warranty for sealing of penetrations? Has the original installer been notified?
SOW.13 |  | Will there a dumpster be required and for how long?
SOW.14 |  | How often and long will a truck be required at the loading dock?
SOW.15 |  | Can the truck be moved if a delivery comes in unexpectedly?
SOW.16 |  | Does it include post work clean-up?
SOW.17 | IT SOW | Does the plan address the following:
SOW.18 |  | Removal of racks or other IT furniture?
SOW.19 |  | Removal of network cabling? [may not be required]
SOW.20 |  | Removal of wireless access points?
SOW.21 |  | Equipment on the roof [e.g. attenae, dish, microwave]?
Architectural
A.1 | Raised Floor | Have you determined whether the raised floor needs to be removed?
A.2 |  | If the intention is to re-use the raised floor:
A.3 |  | Does it have the proper performance attributes for the intended use?
A.4 |  | What components will have to be replaced? [e.g. perforated panels, panels with cable cutouts, understructure, etc.)
A.5 |  | If yes, does the removal costs include disposal costs?
A.6 |  | Can it be re-sold to an access floor recycling company to reduce removal costs?
A.7 |  | Are there railings and ramps that must be removed?
A.8 | Floor | Will the existing raised floor adhesive need to be scraped from the floor? [adhesive clumps could adversely affect new floor covering]
A.9 | Walls | Are there provisions to repair wall finishes where equipment and signage will be removed?
A.10 |  | Are there provisions to patch wall penetrations above and below access floor?
A.11 |  | Do some walls have to be removed because they sit on top of the raised floor?
A.12 |  | Will some walls have to be removed? [e.g. man-trap entrance]
A.13 | Ceilings | Are there grilles in the ceiling (vs. standard tiles) because the plenum above it was used for return air?
A.14 |  | Has it been determined the quantity of ceiling tiles that will need to be replaced due to the removal of smoke detectors, suppression agent nozzles?
A.15 | Cable Tray | Is there cable tray that will have to be removed? [below the access floor, above the ceiling, or in the data center space]
A.16 | Special Furniture | Is there special furniture [e.g. console, NOC, etc.] that will have to be removed?
Mechanical
M.1 | Interior | Do you have a contractor to remove the CRACs/CRAHs?
M.2 |  | Does the contractor have an approved plan to address refrigerant/glycol/etc. removal?
M.3 |  | Can the CRACs/CRAHs be removed via existing paths and elevators?
M.4 |  | Will ductwork have to be removed?
M.5 |  | Will piping have to be removed?
M.6 |  | Will roof penetrations be sealed while maintaining roof warranty?
M.7 |  | In addition to the data center, are there other rooms which contain CRACs that will have to be removed? [UPS, NOC, etc.]
M.8 | Exterior | Is there a plan to remove heat rejection equipment?
M.9 |  | Does this include pumps (if applicable)?
M.10 |  | If it is on the roof, has there been designated an area to position a crane?
M.11 |  | If a crane is required, will this work need to be performed after hours? Has the duration been determined?
M.12 |  | Is a permit required for the crane?
M.13 |  | Will the property manager require that roof curbs or steel structure supporting the heat rejection equipment be removed?
M.14 |  | Will the property manager require the removal of screening?
M.15 |  | If the heat rejection equipment is on grade, will the property manager require the removal of walls, concrete pad, bollards, etc.?
Electrical
E.1 | Generator | Will the generator need to be removed?
E.2 |  | Can the generator and ATS be re-sold to reduce the cost of the decommission work?
E.3 |  | Is there a separate fuel tank that needs to be removed?
E.4 |  | Will the fuel need to be removed from the generator sub-base fuel tank before it is transported?
E.5 |  | Is the ATS included in the removal plan?
E.6 |  | Are n?there panels down-stream of the ATS that will need to be supplied by a another panel that will remai
E.7 |  | Will you need to remove the screening and concrete pads?
E.8 | Switchgear | Will switchgear dedicated to the data center have to be removed?
E.9 |  | To what extent? In electrical room, panels in the data center?
E.10 |  | Is all applicable conduit and wire going to be removed per the latest NEC?
E.11 |  | Does the contractor's SOW include capping holes in panels where conduit is removed?
E.12 | UPS | Does the contractors SOW include a formal verification that the batteries will be disposed of in an approved (DOT/EPA) manner?
E.13 |  | Can the UPS be re-sold to reduce the cost of the decommission work?
E.14 | PDUs | Can the PDUs be re-sold to reduce the cost of the decommission work?
E.15 | EPO | Does the Emergency Power Off (EPO) circuit have to be removed?
E.16 | Exit Buttons | Do request for exit buttons have to be removed?
E.17 | Cameras | Will cameras have to be removed?
Fire Protection
FP.1 | Pre-Action | Will you have to remove the pre-action sprinkler system and convert it to wet sprinkler?
FP.2 |  | If yes, does the scope include removal of associated valving and compressor (typically located in a remote closet)?
FP.3 |  | If yes, then will you have to remove the associated smoke detectors and control panel?
FP.4 | Gaseous | Does your plan include sending the gaseous agent to a recycling company to reduce the cost of the decommission work?
FP.5 |  | Does your plan include removal of piping [above ceiling and below raised floor]?
FP.6 |  | Does your plan include removal of control, panel, horns, strobes, aborts, pull stations?
FP.7 |  | Does your plan include removal of signage inside and outside of all areas that have systems?
FP.8 | Air Sampling | Will the system have to be removed including panel(s) and piping?
Miscellaneous
Mi.1 | Phones | Will you have to remove phones at exits?
Mi.2 | Card access | Will you have to remove card access?
Mi.3 |  | If you own the card access system, will the property manager buy it?
Mi.4 | Network | Will you have to remove network cabling?
Mi.5 | Roof | Do you have any antennae, dishes, etc., that need to be removed?
Response tally of issues/items that require follow-up
|  | Total Responses | 1
|  | Not Addressed | 1
|  | TBD | 0

## Response Drop-down
Response Column Drop-down list
Addressed
Not Addressed
TBD
NA